## Slide 1
MACHINE LEARNING CAPSTONE PROJECT
SolarSense
SCADA Telemetry Intelligence & Machine Learning Power Forecasting
136,472
telemetry records
22
inverter strings
2
solar plants
34
days · 15-min
SCADA is Supervisory Control and Data Acquisition.

## Slide 2: Core objectives, methods and contributions
0. ABSTRACT OF THE PROJECT
1
Utility-scale SCADA ingestion
136,472 records, 2 plants, 34 days at 15-min intervals
2
Understanding sensor gap challenge
Weather dropouts (82 slots in Plant 1) bias naive fills
3
Physics-validated 3-tier imputation
Spline, diurnal match, night zero-clamp; RMSE 0.108 kW/m²
4
Cross-plant electrical calibration
Fixed a 10× DC artifact; efficiency 97.72%
5
Dimensionality reduction via PCA
Top 3 retain 96.17% of variance
6
Unsupervised clustering & DBSCAN
3 generation regimes; 4.4% density outliers isolated
7
Remote anomaly detection (IPI)
Isolation Forest 3.47%; one inverter at −15% yield
8
Multi-model supervised classification
LR, DT, RF reach 98.01% 5-fold CV accuracy
9
High-accuracy sub-hourly forecasting
HistGB R² 0.9625, MAE 28.77 kW, MAPE 9.1%, no leakage
10
Full-stack deployed system
9-stage web platform, explainable API, audit logs

## Slide 3: Dataset and sensor channels
1. DATASET
136,472
SCADA records (P1 68,778 · P2 67,698)
22 strings
independent string inverters
15-min
granularity · May–June 2020
DATE_TIME & PLANT_ID
Master synchronization key
DC_POWER / AC_POWER
Inverter input; AC is the target
DAILY & TOTAL YIELD
Energy meters, drive IPI
IRRADIATION
r = 0.97 with AC power
MODULE & AMBIENT TEMP
~0.4%/°C derating above 25°C
TEMP_DIFF (ΔT)
Engineered cell-heating predictor

## Slide 4: A 10× scaling bug hid 97.72% efficiency
2. EXPLORATORY DATA ANALYSIS
Plant 1 DC power fix
9.7%
apparent efficiency
97.72%
after ÷10 correction
Daylight DC 3,147 kW vs AC 307.8 kW exposed the artifact.
Both plants now match.
Night (18:30–05:30) is physically zero; modeling is daylight-only to avoid inflated R².
Chart: Correlation with AC power (Pearson r)
| Ambient temp | Temp diff (ΔT) | Module temp | Irradiation | DC power
Pearson r | 0.54 | 0.76 | 0.81 | 0.97 | 0.99

## Slide 5: 3-tier imputation beats naive filling
3. MISSING VALUE REPLACEMENT
Night gaps
Short gaps ≤ 1 h
Long gaps > 1 h
Zero-clamp irradiation (18:30–05:30)
Time linear spline captures cloud trajectory
Diurnal profile matching, same-hour mean
Forward fill can overestimate power by >200% across a 2-hour cloudy gap. Gaps: 82 missing slots in Plant 1, 5 in Plant 2.
Chart: Irradiance RMSE (kW/m², lower is better)
| Diurnal match | Forward fill | Linear spline
RMSE | 0.165 | 0.13 | 0.108

## Slide 6: 3 PCs retain 96.17% of variance
4. PRINCIPAL COMPONENT ANALYSIS
Chart: Explained variance by component (%)
| PC1 | PC2 | PC3 | PC4 | PC5+6
Variance % | 57.62 | 21.92 | 16.62 | 3.12 | 0.72
96.17%
cumulative with top 3 PCs (optimal)
PC1
Solar flux: irradiance + module temp
PC2
Thermal gradient: ΔT + ambient
PC3
Diurnal solar angle: hour of day

## Slide 7: Supervised models: boosting wins
5. SUPERVISED MODELS
Ridge regression
Baseline, α = 1.0. R² 0.8741, MAE 46.23 kW, RMSE 68.54 kW. Exports coefficients for instant ± kW explanations.
Logistic regression
High vs normal output regime. Accuracy 96.25%, precision 97.77%, recall 94.64%, F1 96.18%.
Tree ensembles
DT 96.53% acc. RF 96.50% acc. HistGB champion: R² 0.9625, MAE 28.77 kW, MAPE 9.1%, trains in 0.62 s.

## Slide 8: Regimes, outliers and faulty hardware
5. UNSUPERVISED MODELS
K-Means (k=3)
Morning/evening ramp: 9,863. Peak midday: 19,298. Diffuse/cloudy: 9,467 intervals.
DBSCAN
eps 0.8, min_samples 25. 220 outliers (4.4%): sensor spikes and inverter trips at peak sun.
Isolation Forest + IPI
3.5% contamination flags 1,341 rows. 21 inverters healthy; one at 88.3% IPI, a soiling or string fault.
IPI = (E_daily,i ÷ Median E_daily) × 100%

## Slide 9: HistGradientBoosting is the champion
6. ACCURACY & METRICS
Chart: Holdout R² (AC power)
| Ridge | Random Forest | HistGB
R² | 0.8741 | 0.9571 | 0.9625
HistGB: MAE 28.77 kW · RMSE 38.93 kW · MAPE 9.1%
Trains in 0.62 s vs 8.42 s for Random Forest
Random Forest confusion matrix
3,812
True negative
73
False positive
196
False negative
3,645
True positive
7,726 test rows · accuracy 96.50% · precision 0.9804 · recall 0.9490 · F1 0.9644

## Slide 10: Validation: stable folds and zero leakage
7. CROSS VALIDATION
Chart: 5-fold mean CV accuracy (%)
| Logistic | Decision Tree | Random Forest
CV acc | 97.38 | 97.9 | 98.01
Shuffled K-Fold leaks
Random shuffling lets future telemetry into training folds and inflates metrics.
Chronological 80/20
Earliest 80% trains; latest 20% is a sealed holdout, evaluated once.
Train-only preprocessing
Imputers and scalers fit on training data alone, so R² = 0.9625 is honest.

## Slide 11
DEPLOYMENT & CONCLUSION
SolarSense in production
9-stage web app
Flask + Jinja2, plant toggle, imputation lab, analytics, inference, Chart.js visuals.
Explainable API
POST /api/predict and GET /api/bundle with ± kW attributions from Ridge weights.
CleanTech value
Fixes IoT dropouts for community solar billing; remote soiling alerts cut site inspections.